## Slide 2: Pressure relief systems and Safety Instrumented Systems COMMON WEAKNESSES IN FIELD IMPLEMENTATION
William G. Bridges Stephen Bridges

## Slide 3
William Bridges Process Improvement Institute - President
STUDIES
BS & MS Chemical Engineering
Co-invented LOPA
Certified functional safety professional
Process safety expert
Human factors expert
EXPERIENCE +40 years
13 years in plant, 2 as Operator
+250 Unit PHAs
+8000 PHAs managed
+1000 LOPAs
+1000 SIL Verification/Assessments
+3500 trained PHA/LOPA leaders
PUBLICATIONS
Main author of
5 other CCPS Guidelines books – contributing author
+50 Papers presented

## Slide 4
DESIGN Failing to account for common cause failures of similar components
Configuration | PFD Calculation (for β < 0.2)
NooN | 
MooN | 
Configuration | PFD Calculation (for β < 0.2)
NooN | 
MooN | 
M | N | PFD (MooN)
1 | 1 | 0.0100
1 | 2 | 0.0011
2 | 3 | 0.0014
1 | 3 | 0.0010
3 | 3 | 0.0310
3 | 5 | 0.0010
4 | 5 | 0.0023
5 | 5 | 0.0510
14 | 15 | 0.0150
15 | 15 | 0.1510
EXAMPLES

## Slide 5
Dependence | Same person? | Close in time? | Same visual frame? | Writing required? |  | Repeating failure
Zero | No | Yes/No | Yes/No | Yes/No |  | 
Zero | Yes | No (+2 days) | Yes/No | Yes/No |  | 
Low | Yes | Low (+1 day) | No | Yes |  | 
Moderate | Yes | Moderate (+4h) | No | No |  | 
High | Yes | Yes (<2h) | No | No |  | 
Complete | Yes | Yes (<2h) | Yes | Yes/No |  | 
Dependence | Same person? | Close in time? | Same visual frame? | Writing required? |  | Repeating failure
Zero | No | Yes/No | Yes/No | Yes/No |  | 
Zero | Yes | No (+2 days) | Yes/No | Yes/No |  | 
Low | Yes | Low (+1 day) | No | Yes |  | 
Moderate | Yes | Moderate (+4h) | No | No |  | 
High | Yes | Yes (<2h) | No | No |  | 
Complete | Yes | Yes (<2h) | Yes | Yes/No |  | 
ITPM PLANNING Failing to control common-cause human error (dependent human errors)
For Complete dependence, the Probability of repeating a mistake is 1

## Slide 6
BASELINE ESTIMATION Failing to account for errors during human interventions
 | 0.01 | 
 | 0.01 | 
 | 0.04 | Probability of leaving at least one block valve closed (without independent audit)
 | 0.05 | 
 | 0.01 | 
 | 0.01 | 
 | 0.04 | Probability of leaving at least one block valve closed (without independent audit)
 | 0.05 | 
EXAMPLE
(This term should not be ignored)
(This term should not be ignored)

## Slide 7
CASE STUDY: Results of Third-Party Inspection of CSO Block Valves for PSVs
 |  |  | UPSTREAM |  |  |  |  |  | DOWNSTREAM |  |  |  |  | 
Unit | Total PSVs | # of PSVs audited | # BVs | # BVs wrong | # CS on BVs | # CS missing | % BV wrong | % CS missing | #BVs | #BVs wrong | #CS on BVs | #CS missing | % BV wrong | % CS missing
A | 534 | 363 | 238 | 0 | 237 | 1 | 0 | 0.4 | 154 | 0 | 153 | 1 | 0 | 0.7
B | 65 | 49 | 35 | 0 | 35 | 0 | 0 | 0 | 22 | 0 | 22 | 0 | 0 | 0
C | 276 | 211 | 43 | 0 | 40 | 3 | 0 | 7 | 154 | 0 | 7 | 0 | 0 | 0
D | 548 | 267 | 132 | 0 | 89 | 43 | 0 | 32.6 | 62 | 0 | 31 | 31 | 0 | 50
TOTAL | 1423 | 890 | 448 | 0 | 401 | 47 | 0 | 10 | 392 | 0 | 213 | 32 | 0 | 12.7
A SABIC affiliate

## Slide 8
THANK YOU
WILLIAM (Bill)
BRIDGES
wbridges@piii.com